## Slide 1
G4U
TECHNICAL SELECTION
Building Performance, Proven.
AI energy
management
for better buildings
Technical selection guide for existing office buildings.
AI Energy Management
Retrofit Engineering
Managed Performance
Illustrative building scene
Notes: Use this deck for technical selection. Confirm the customer's building systems, operating authority, available data and decision priorities. The integrated solution combines AI energy management, retrofit engineering and managed performance. The cover is an illustrative building scene.

## Slide 2
G4U
TECHNICAL SELECTION
Define the operating boundary before choosing the tools
Begin with one existing office building and owner-controlled common services.
G4U Technical Services L.L.C. / Technical selection
02
One agreed building performance scope
Measurable systems
Agreed operating authority
01
Electricity, water and cooling consumption
02
On-site plant or customer-side district cooling
03
Owner-controlled HVAC and common areas
04
Relevant comfort and equipment-availability data
Tenant-controlled areas and future extensions follow a separate agreed scope.
Notes: Define cooling supply, billing boundaries and operating responsibility first. Tenant-controlled areas are outside the initial scope. Electricity, water and cooling require distinct units and measurement boundaries.

## Slide 3
G4U
TECHNICAL SELECTION
The energy core connects to existing building systems
Separate software analysis from field integration, construction and site execution.
G4U Technical Services L.L.C. / Technical selection
03
AI energy core
Energy facts, diagnostics, forecasting, scenarios, optimization, M&V, SLA and AI dialogue.
Existing digital systems
IoT, BMS/IBMS and FM provide data, operating context and external action status.
Engineering delivery
Metering, commissioning, control implementation and equipment works are separate delivery scopes.
Optional extensions
Connected services and 3D digital twins belong to the wider product family, not the core energy software.
Notes: The approved energy-product boundary excludes IoT collection hardware, FM/work orders, IBMS, specific control execution/interfaces and 3D twin. The solution family can provide those through separately defined workstreams. The core includes 2D analytical logic views.

## Slide 4
G4U
TECHNICAL SELECTION
Four workspaces support the operating decision cycle
The design connects everyday analysis with action and performance review.
G4U Technical Services L.L.C. / Technical selection
04
Understand
Overview, Energy Explorer, meter balance and 2D system/equipment views.
Investigate
Data quality, anomaly evidence, root-cause hypotheses and impact assessment.
Improve
Forecasts, what-if scenarios, energy conservation measures and approved action drafts.
Verify
Baseline and M&V, Triple SLA, fixed reports and evidence packages.
Notes: Describe these as the configured solution design. Existing metering/basic analysis forms the foundation; advanced energy workflows are introduced through project configuration and acceptance. Explain how a user moves from an anomaly to an action rather than reading every menu.

## Slide 5
G4U
TECHNICAL SELECTION
Professional tools and AI dialogue share one evidence layer
The architecture makes the source of a number and the route to an action visible.
G4U Technical Services L.L.C. / Technical selection
05
Site information
Telemetry
Meter topology
Operating calendars
Approved documents
Energy analysis
Data quality and semantics
Versioned analytical tools
Derived results and evidence
Model and tool registry
User and AI workflow
Investigate and compare
Explain and draft
Review and approve
Export and follow up
Approved intent goes to the external execution workflow. Site safety remains independent.
Notes: This is a logical architecture, not an interface specification. The agent uses professional tools rather than generating formal numbers from prose. External systems own collection, FM execution and site control. The approved design preserves source data and versioned derived results.

## Slide 6
G4U
TECHNICAL SELECTION
Reliable energy facts begin with semantics and quality
A useful trend needs the right object, unit, time interval and measurement state.
G4U Technical Services L.L.C. / Technical selection
06
Point and object meaning
Map building, system, equipment, meter and common area to consistent engineering semantics.
Time and units
Align interval/cumulative readings, timestamps, time zones and electricity, water and cooling units.
Quality and balance
Check completeness, range, flatline, spikes, drift and consistency with the meter hierarchy.
Measured and estimated
Keep raw readings intact; identify derived or imputed values and their uncertainty.
Notes: A data-quality score is decomposable into the underlying checks. Estimated values remain identified. Missing or unreliable critical points reduce analytical scope rather than silently becoming a formal measurement.

## Slide 7
G4U
TECHNICAL SELECTION
Model Packs reuse engineering logic and adapt to the site
Configure a tested equipment family rather than writing a new model for every machine.
G4U Technical Services L.L.C. / Technical selection
07
Reusable family
Object semantics, physical constraints, features, rules and candidate algorithms.
Site configuration
Equipment subtype, topology, operating modes, calibrated parameters and diagnostic signatures.
Three depth levels
Tier 0: rules/KPIs. Tier 1: physical/statistical models. Tier 2: ML and optimization.
Acceptance and operation
Backtest, boundary tests, shadow operation, expert approval and monitored release.
Notes: The seven Model Packs cover whole building/main meter, chiller, chilled/condenser-water pumps, cooling towers, AHU, fresh/exhaust air and common-area terminals. The design prioritizes whole-building, chiller, pump and AHU packs, with the others configured to project need and data. Algorithm family reuse does not remove the need for site calibration.

## Slide 8
G4U
TECHNICAL SELECTION
Cooling-side models explain plant and equipment performance
Main methods come first; alternatives are selected when data and validation justify them.
G4U Technical Services L.L.C. / Technical selection
08
Whole building / meters
Change-point regression and energy-balance reconciliation. Alternatives: GAM or constrained gradient boosting.
Chillers
Heat balance, COP, kW per refrigeration ton and calibrated performance curves. Alternatives: Gordon-Ng or gradient boosting.
Water pumps
Affinity laws, hydraulic/system curves and site calibration. Alternatives: constrained regression or hydraulic-network models.
Cooling towers
Range/approach and wet-bulb-normalized performance. Alternatives: Merkel/NTU or constrained regression.
Notes: These are the main and alternative methods in the approved taskbook. Model suitability depends on available points, operating modes and validation. Efficiency calculations require credible power and cooling/flow measurements. A virtual meter remains an estimate rather than replacing a formal meter without a separately agreed measurement method.

## Slide 9
G4U
TECHNICAL SELECTION
Airside models connect energy use with operating conditions
Sequence checks and physical relationships provide an interpretable starting point.
G4U Technical Services L.L.C. / Technical selection
09
AHU / FAHU
Air and heat balance, operating-sequence rules and response residuals. Alternatives: grey-box dynamics or gradient boosting.
Fresh and exhaust air
Schedules, state rules and CO2/pressure/flow proxies. Alternatives: mass-balance inversion or occupancy models.
Common-area terminals
Zone rules and first-order RC thermal response. Alternatives: constrained regression or GAM.
Indoor environment
Contract-configured temperature/humidity and occupied-time compliance. PMV/PPD or adaptive methods are optional with sufficient inputs.
Notes: Model coverage stays within owner-controlled equipment and common areas. Indoor-environment methods must match the actual input quality and agreed scope. Basic diagnostics can remain useful when a site lacks every advanced airflow or CO2 sensor.

## Slide 10
G4U
TECHNICAL SELECTION
Different analytical jobs use different model families
Keep a formal baseline distinct from a dynamic operating forecast.
G4U Technical Services L.L.C. / Technical selection
10
Formal baseline
Multivariable change-point regression with residual and holdout checks. Alternatives: GAM, calibrated simulation or constrained ML.
Anomaly detection
Engineering rules, robust thresholds, baseline residuals and change points. ML detectors add supporting evidence.
Root-cause assessment
System causal graphs, fault signatures and evidence scoring. The AI agent organizes competing hypotheses and checks.
Load forecasts
Gradient boosting with calibrated prediction intervals. Alternatives: GAM, SARIMAX or grey-box RC models.
Notes: The main methods are taken from the approved energy algorithm design. The frozen formal M&V model and the dynamic operational model serve different purposes and may use different update rules. Forecast validation uses time-based splits and compares simple baselines.

## Slide 11
G4U
TECHNICAL SELECTION
Use frequent local analysis and deeper AI review at different speeds
Cloud dialogue does not become a dependency for every high-frequency calculation.
G4U Technical Services L.L.C. / Technical selection
11
Local professional tools
Physical, rule, statistical, ML and optimization analysis, typically at 1–15-minute cadence.
Local small models
Sensitive, repetitive or low-latency classification and summarization tasks.
Cloud or local orchestrator
Tool-assisted investigation on significant events, on demand, or in daily/weekly review.
Human decisions
Approval of formal baselines, performance reports, high-risk intent and production model releases.
Notes: These are configuration choices, not universal response-time guarantees. Cadence follows the measurement signal, use case and deployment. Local analysis remains available when cloud AI is disconnected, within the agreed local configuration.

## Slide 12
G4U
TECHNICAL SELECTION
The assistant shows the evidence behind its recommendation
G4U Technical Services L.L.C. / Technical selection
12
“Why did this chiller's efficiency change after 14:00?”
Bind context
Confirm the site, equipment, time window and quality of the readings.
Use tools
Compare load, temperatures, efficiency and likely fault signatures.
Explain
Present supported causes, counter-evidence and open checks.
Prepare action
Draft a verification plan or Energy Action for authorized review.
Illustrative investigation workflow
Notes: A good answer binds scope, tools, evidence, uncertainty, impact and next action. If flow or temperature data is unreliable, the assistant investigates measurement quality before claiming equipment degradation. The example is a workflow illustration.

## Slide 13
G4U
TECHNICAL SELECTION
Optimization balances energy with practical operating limits
Use model outputs to evaluate a feasible strategy before site execution.
G4U Technical Services L.L.C. / Technical selection
13
What-if scenarios
Use frozen prediction, physical performance or engineering-measure models appropriate to the question.
Rolling optimization
Constrained Model Predictive Control (MPC). Discrete equipment choices may use MILP/MINLP approximations.
Operating constraints
Respect comfort, equipment capacity, minimum run times, redundancy and approved operating limits.
Decision output
A proposed target, expected effect, constraints, approval route, rollback and verification window.
Notes: The core product generates structured intent; actual device commands and control implementation are external. Primary optimization methods are MPC with appropriate constrained discrete formulations. Rule-based optimization and Bayesian optimization are alternatives; safe reinforcement learning is not implied as the default production method.

## Slide 14
G4U
TECHNICAL SELECTION
A versioned M&V ledger makes savings reproducible
Measurement and Verification (M&V) compares measured use with an approved, adjusted baseline.
G4U Technical Services L.L.C. / Technical selection
14
Baseline
Boundary, historical data, model candidates and approval.
Adjustment
Weather, calendars and approved material operating changes.
Reporting
Measured use, calculation version, uncertainty and review.
Savings = adjusted baseline minus reporting use, with approved non-routine adjustments.
Notes: The design uses a whole-building/main-meter approach and isolated-measure verification where appropriate. Record non-routine adjustments separately and avoid counting a system measure twice in an aggregate. The calculation and evidence versions are retained so a reviewed result can be reproduced.

## Slide 15
G4U
TECHNICAL SELECTION
Three service outcomes keep the performance review balanced
Each outcome retains its own measurement, boundary and review status.
G4U Technical Services L.L.C. / Technical selection
15
01
Energy & Water Performance
Normalized resource use and agreed savings/performance measures.
02
Indoor Environment
Agreed occupied-time environmental conditions in the service area.
03
Contracted Equipment Availability
Availability of included equipment when its service is required.
Review the three outcomes separately, then apply the agreed contract rules.
Notes: Equipment availability is not inferred from a single run-status point. Planned maintenance, capacity and responsibility rules belong to the agreed equipment scope. An aggregate green score does not replace the three underlying measurements.

## Slide 16
G4U
TECHNICAL SELECTION
Increase action authority only after the site is ready
L0–L3 describe energy-system intent, while external systems retain control execution.
G4U Technical Services L.L.C. / Technical selection
16
L0
Analyze and explain.
L1
Prepare a recommendation.
L2
Submit approval-gated intent.
L3
Generate intent within an approved envelope.
Existing control systems retain interlocks, safety, final commands and rollback execution.
Notes: Choose the level for each site/use case. Higher intent authority requires data quality, confirmed operating ownership, tested constraints, external execution readiness, approval and rollback. A language model cannot grant its own permission.

## Slide 17
G4U
TECHNICAL SELECTION
Configure local and cloud responsibilities to the customer's needs
Data policy, resilience and operating requirements determine the deployment.
G4U Technical Services L.L.C. / Technical selection
17
At the building
Quality checks
Selected local analysis
Local state and fallback
Existing control systems
Energy platform
Versioned data and tools
Model Pack configuration
Reports and approvals
Audit and recovery
AI model services
Local small-model tasks
Approved cloud context
Tool-assisted dialogue
Budget and access policy
Agree data location, cloud access, recovery targets and operating ownership.
Notes: This is a logical deployment selection view rather than a detailed infrastructure/interface design. Cloud context is minimized to needed results, excerpts and selected windows. Recovery targets and retention periods are agreed to the project; no arbitrary RPO/RTO is asserted here.

## Slide 18
G4U
TECHNICAL SELECTION
Governance makes model improvement controlled and reviewable
Learning feeds candidates, evaluation and approved release.
G4U Technical Services L.L.C. / Technical selection
18
Evidence and knowledge
Scope retrieval to the site and user. Keep approved facts distinct from conversation state or suggestions.
Permissions and audit
Allowlisted tools, object scope, structured parameters and recorded formal actions.
Evaluation and release
Backtest, benchmark, security/boundary tests, shadow operation and expert approval.
Monitor and recover
Watch error, drift, false alarms and user corrections; use rollback or a new tested candidate.
Notes: The target design registers models, prompts, tools, policies and Model Packs. Production improvement is not an uncontrolled self-editing process. Security and calculation gates are verified with test evidence before release.

## Slide 19
G4U
TECHNICAL SELECTION
Energy Actions connect software findings with engineering delivery
One measure carries its assumptions, implementation status and verification plan.
G4U Technical Services L.L.C. / Technical selection
19
Define the measure
Describe the operating issue, proposed change, affected assets and expected energy effect.
Check the site
Confirm comfort/safety constraints, equipment condition, access and construction implications.
Deliver the work
Coordinate commissioning, equipment/control works and external FM implementation.
Verify and operate
Record acceptance, compare results and hand the measure into managed performance.
Notes: The software tracks Energy Actions and external implementation status; it does not replace FM dispatch/work orders. Engineering includes field design, procurement and construction as separately contracted delivery, not as an AI software feature.

## Slide 20
G4U
TECHNICAL SELECTION
A phased deployment aligns capability with data and acceptance
Build from the metering and analysis foundation toward advanced energy workflows.
G4U Technical Services L.L.C. / Technical selection
20
01
Foundation
Confirm objects, readings, quality, energy views and the initial boundary.
02
Site acceptance
Calibrate Model Packs, baseline and diagnostics; test agent tools and shadow workflows.
03
Advanced operation
Introduce forecasts, optimization and higher intent levels after the agreed gates.
Configured scope / replay and shadow evidence / acceptance record / operating and recovery plan
Notes: Established digital platforms and foundational energy metering/analysis form the starting point. Advanced energy functions follow a defined deployment roadmap and project acceptance. The 90-day assessment informs the configuration, deployment and investment path.

## Slide 21
G4U
TECHNICAL SELECTION
Reference experience spans energy, integration and engineering
Anonymous project records demonstrate relevant delivery experience.
G4U Technical Services L.L.C. / Technical selection
21
Corporate headquarters
13.3%
Annual electricity savings
Integrated smart-building and energy-management applications.
Large commercial complex
23%
Average HVAC energy savings
Central HVAC optimization and coordinated operation.
Notes: Source: anonymous project operating records. The metrics have different scopes. A further landmark commercial-tower reference combines cooling modernization, AI optimization, monitoring, digital asset management and managed operation without a published numerical result.

## Slide 22
G4U
TECHNICAL SELECTION
Agree the selection questions and the next technical step
Use the discovery record and readiness checklist to turn interest into a scoped project.
G4U Technical Services L.L.C. / Technical selection
22
Boundary and authority
Which meters, HVAC systems and common areas are included? Who can approve an operating change?
Data and deployment
Which points are reliable? What are the time/unit meanings, access conditions and cloud policies?
Performance and acceptance
Which outcomes matter? How will baseline, models, workflows and the service be accepted?
Delivery and ownership
Who supplies site access, engineering/FM coordination and the decisions for the assessment?
Notes: Close by recording a candidate building, decision owners, a minimal data request and the next technical meeting/site visit. Contacts stay blank until formally supplied. The goal is an agreed scope and acceptance path, not an unsolicited fixed price or saving promise.